## Slide 1
ENHANCEMENT OF DISTRIBUTION SYSTEMS PERFORMANCE USING MODERN OPTIMIZATION TECHNIQUES
MENOUFIA UNIVERSITY
FACULTY OF ENGINEERING, SHEBIN EL-KOM
ELECTRICAL ENGINEERING DEPARTMENT
Supervised by:
Dr. Mohamed Taha Mouwafi

## Slide 2: Team work
Moustafa Mohamed Abdelghani Abdalla Shahin
Mohamed Khaled Ahmed Soltan
Mohamed Rabie Abdelhamid Mohamed Elshiekh
Moustafa Mohamed Abdelghani Nada
Mohamed Fekry Mohamed Abdelwareth Zahran
Mohamed EmadAldean Abdelnabi Abdallah
Mohamed Ali Elsayed Abdelgleil
Mohamed Eldesoky Ahmed Halema
Mohamed Ragab Abdelmoati Khafaga
Moustafa Ahmed Sabry Alashmawi
Islam Gamal Hussien Alagha

## Slide 3
Project outlines
CHAPTER 1 Introduction
CHAPTER 2 Distributed Generations and Capacitors Technologies
CHAPTER 3 Problem Formulation
CHAPTER 4 Archimedes Optimization Algorithm
CHAPTER 5 Applications and Results
CHAPTER 6 Conclusions

## Slide 4: CHAPTER 1
INTRODUCTION

## Slide 5
INTRODUCTION
The optimization can be defined as a part of the applied or numerical mathematics or a method for system design by computer in accordance with either one stress theoretical aspect (existence of the optimum solution conditions) or the practical aspect (procedures for obtaining the optimum solution).
Archimedes Optimization Algorithm is based on Archimedes’ principle. AOA emulates the behavior of many objects, which have different densities and volumes, immersed in the same fluid and each one tries to reach equilibrium state.
Capacitor banks are commonly used in a distribution system to provide reactive power locally, resulting in reduced maximum kVA demand, improved voltage profile, reduced line/feeder losses and decreased payments for the energy.

## Slide 6
DG generates electricity from many small energy sources located close to the load being served.
DG can lower costs, enhance efficiency, improve reliability, reduce emissions, or expand their energy options.
The backward/forward sweep (BFS) algorithm is one of the most common ways used for load flow calculations in distribution system , involves mainly an iterative three basic steps based on Kirchhoff's current law (KCL) and Kirchhoff's voltage law (KVL).
INTRODUCTION

## Slide 7
CHAPTER 2
DISTRIBUTED GENERATIONS AND
CAPACITORS TECHNOLOGIES

## Slide 8
Distributed Generations
DG generally applies to relatively small generating units sited at or near customer sites to meet specific customer needs to support economic, operation of the existing distribution grid, or both.
Types of DGs
Conventional fossil fuel based combustion engines.
Renewable energy including wind, photovoltaic cells, micro turbines, combined heat and power (CHP) or hybrid.

## Slide 9
Applications of DGs
Standby power
Combined heat and power
Peak shaving
Grid support
Stand alone
Capacitor Banks
Capacitor banks applied to distribution systems can be fixed or switched depending on the load conditions.
Fixed capacitor banks for minimum load condition. While, Switched capacitor banks for load levels above the minimum load and up to the peak load.

## Slide 10
Benefits of capacitor banks
Reactive power support.
Voltage profile improvements.
Line and transformer loss reduction.
Release of power system capacity.
Savings due to reduced energy losses.

## Slide 11
CHAPTER 3
PROBLEM FORMULATION

## Slide 12
Objective function
Problem Formulation
where,
PLoss is the total real power loss to be minimized
Pi and Qi are the net active and reactive power at bus i
Vi and Vj are the voltage magnitudes at buses i and j
δi and δj are the phase angle of the voltages at buses i and j
Rij is the line resistance between buses i and j
Nb is the number of system buses.

## Slide 13: Load balancing constraint
Pgj and Qgj are the active and reactive power output from the generator at bus j
Pdj and Qdj are the active and reactive power demand at bus j
Vi and Vj are the voltages at sending end i and receiving end j
Yij and θij are the admittance magnitude and angle between buses i and j
δi and δj are the phase angles of voltages at buses i and j
System constraints
Equality constraint

## Slide 14
Overall Power factor constraint
Number of DGs constraint
Number of capacitors constraint
Bus voltage constraint
Inequality constraints

## Slide 15: Capacitor size constraint
Total active and reactive power constraints
DG size constraint

## Slide 16: CHAPTER 4
Archimedes Optimization ALGORITHM

## Slide 17
Archimedes Optimization Algorithm
Archimedes Optimization Algorithm (AOA) is based on Archimedes’ principle which states that “Any object, totally or partially immersed in a fluid or liquid, is buoyed up by a force equal to the weight of the fluid displaced by the object.”. AOA emulates the behavior of many objects, which have different densities and volumes, immersed in the same fluid and each one tries to reach equilibrium state.

## Slide 18
AOA Theory

## Slide 19: AOA Theory
If we assume that many object are immersed in the same fluid and each one of them tries to reach equilibrium state. The object will be in the equilibrium state if the buoyant force equal to the object’s weight :
Where is the density, is the volume, and is the gravity or acceleration, subscripts and are for fluid and immersed object, respectively. This equation can be rearranged as:

## Slide 20: AOA Theory
If there is another force influenced on the object like collision with another neighbouring object (), the equilibrium state will be:

## Slide 21: AOA algorithmic steps
Step 1: initialize the positions of all objects using
Step 2: update densities, volumes using

## Slide 22: AOA algorithmic steps
Step 3: calculate Transfer operator and density factor using
Step 4.1: Exploration phase (collision between objects occurs)
Step 4.2: Exploitation phase (no collision between objects)

## Slide 23: AOA algorithmic steps
Step 4.3: Normalize acceleration
Step 5: update position
Exploration phase
Exploitation phase

## Slide 24: Pseudo code of AOA

## Slide 25: CHAPTER 5
APPLICATIONS AND RESULTS

## Slide 26
APPLICATIONS AND RESULTS
Test systems
34-bus standard radial distribution system .
East Delta Network (EDN) radial distribution system as a part of the Unified Egyptian Network (UEN).
Objective functions
Total power loss minimization
Total voltage deviation minimization

## Slide 27
Case Studies
Case 0: Without DGs and capacitors (i.e., the BFS algorithm results).
Case 1: With only DGs operating at unity power factor (p.f.)
Case 2: With only DGs operating at p.f. = 0.9, means that active and reactive power injections.
Case 3: With only capacitors, means that only reactive power injections.
Case 4: with both DGs at unity power factor and capacitors.
Case 5: with DGs at power factor .9 and capacitors
APPLICATIONS AND RESULTS

## Slide 28
Results and Comments
Total power loss minimization for IEEE-34 system (case 1)
Items | Un-compensated (Case 0) | Compensated (Case 1) |  |  |  |  |  |  |  |  | 
 |  | DPS [10] |  | Analytical Method [11] |  | MBFO [12] |  | GA [13] |  | Proposed procedure | 
Optimal locations and sizes of DGs (kW) | - | 27 | 2500 | 21 | 2884.8 | 21 | 2951.7 | 4 | 500 | 23 | 1847.5
 |  | - | - | - | - | - | - | 7 | 500 | 31 | 1152.5
 |  | - | - | - | - | - | - | 17 | 500 | - | -
 |  | - | - | - | - | - | - | 21 | 500 | - | -
 |  | - | - | - | - | - | - | 25 | 500 | - | -
 |  | - | - | - | - | - | - | 28 | 500 | - | -
Total size | - | 2500 |  | 2884.8 |  | 2951.7 |  | 3000 |  | 3000 | 
Total losses (kW) | 221.752 | 118.8 |  | 93.838 |  | 93.751 |  | 83.84 |  | 74.416 | 
TVD | 0.0483 | 0.0086 |  | 0.0079 |  | 0.0074 |  | 0.0108 |  | 0.0046 | 
Minimum bus voltage(p.u.) | 0.9417 (#27) | 0.9750 (#34) |  | 0.9773 (#34) |  | 0.9777 (#34) |  | 0.9723 (#27) |  | 0.9832 (#27) | 
Maximum bus voltage(p.u.) | 0.9941 (#2) | 1.0034 (#27) |  | 0.9971 (#2) |  | 0.9971 (#2) |  | 0.9972 (#2) |  | 0.9972 (#2) | 
Overall power factor | 0.85 | 0.5967 |  | 0.5205 |  | 0.5058 |  | 0.4949 |  | 0.4949 | 

## Slide 29
Results and Comments
Total power loss minimization for IEEE-34 system (case 2)
Items | Un-compensated (Case 0) | Compensated (Case 2) |  |  |  | 
 |  | Analytical Approach [18] |  |  | Proposed procedure | 
Optimal locations and sizes of DGs (kW, kVAR) | - | Locations | DG Size (kW) | - | Locations | DG size (kW)
 |  | 20 | 3231.8 | - | 23 | 1863.3
 |  | - | - | - | 10 | 1136.7
 |  | - | - | - |  | 
Total size | - | - | 3231.8 | - | - | 3000
Total losses (kW) | 221.752 | 49.415 |  |  | 25.348 | 
TVD | 0.0483 | 0.004 |  |  | 0.0023 | 
Minimum bus voltage(p.u.) | 0.9417 (#27) | 0.9832 (#34) |  |  | 0. 9888 (#27) | 
Maximum bus voltage(p.u.) | 0.9941 (#2) | 1.0015 (#20) |  |  | 0.9978 (#2) | 
Overall power factor | 0.85 | 0.85 |  |  | 0. 7552 | 

## Slide 30
Results and Comments
Total power loss minimization for IEEE-34 system (case 3)
Items | Un-compensated (Case 0) | Compensated (Case 3) |  |  |  |  |  |  |  |  | 
 |  | PGSA [14] |  | BFA [15] |  | GA [16] |  | APSO [17] |  | Proposed procedure | 
Optimal locations and sizes of capacitors (kVAR) | - | 19 | 1200 | 9 | 600 | 7 buses | 1629 | 19 | 1050 | 18 | 896.88
 |  | 20 | 200 | 22 | 900 |  |  | 25 | 750 | 9 | 758.562
 |  | 22 | 639 | - | - |  |  | - | - | 24 | 862.755
Total size | - | 2039 |  | 1500 |  | 1629 |  | 1800 |  | 2482.5 | 
Total losses (kW) | 221.752 | 169.167 |  | 169.07 |  | 168.955 |  | 168.023 |  | 160.4252 | 
TVD | 0.0483 | 0.0368 |  | 0.0394 |  | 0.0408 |  | 0.0375 |  | 0.0344 | 
Minimum bus voltage(p.u.) | 0.9417 (#27) | 0.9492 (#27) |  | 0.9503 (#27) |  | 0.9491 (#27) |  | 0.9416 (#27) |  | 0.9503 (#27) | 
Maximum bus voltage(p.u.) | 0.9941 (#2) | 0.995 (#2) |  | 0.9948 (#2) |  | 0.9948 (#2) |  | 0.9949 (#2) |  | 0.9952 (#2) | 
Overall power factor | 0.85 | 0.9842 |  | 0.9588 |  | 0.9658 |  | 0.9738 |  | 0.9965 | 

## Slide 31
Results and Comments
Total power loss minimization for IEEE-34 system (case 4)
Items | Un-compensated (Case 0) | Compensated (Case 4) |  |  | 
 |  | Proposed procedure |  |  | 
Optimal locations and sizes of DGs (KW) | - | 9 |  | 952.8 | 
 |  | 21 |  | 1125.5 | 
 |  | 25 |  | 921.6 | 
Total DGs size |  | 3000 |  |  | 
Optimal locations and sizes of capacitors (KVAR) |  | 7 | 1110.4 |  | 
 |  | 24 | 816.6 |  | 
Total capacitors size | - | 1927 |  |  | 
Total losses (kW) | 221.752 | 18.15 |  |  | 
TVD | 0.0483 | 0.0023 |  |  | 
Minimum bus voltage(p.u.) | 0.9417 (#27) | 0.9892 (#33) |  |  | 
Maximum bus voltage(p.u.) | 0.9941 (#2) | 0.998 (#2) |  |  | 
Overall power factor | 0.85 | 0.8656 |  |  | 

## Slide 32
Results and Comments
Total power loss minimization for IEEE-34 system (case 5)
Items | Base case |  | Case 5 | 
 |  |  | FPA [9] | Proposed method
DG size (kW, kVAR) and location | - |  | 2086, 1292.8 (#26) | 799.3, 387.09 (#31), 946.5, 458.37 (#24), 1254.2, 607.39 (#21)
Capacitor size (kVAR) and location | - |  | 1250 (#26) | 365.568 (#8)
Total size of DGs (kW, kVAR) | - |  | 2086, 1292.8 | 3000, 1452.86
Total size of capacitors (kVAR) | - |  | 1250 | 1112.9
f1 [Loss (kW)] | 221.752 |  | 58.8298 | 17.1153
TVD | 0.0483 |  | 0.007 | 0.0021
Min. voltage (p.u.) | 0.9417 (#27) |  | 0.9751 (#34) | 0.99 (#12)
Overall p.f. | 0.85 |  | 0.8436 | 0.8405

## Slide 33
Results and Comments
Total power loss minimization for IEEE-34 system (Voltage profile)

## Slide 34
Results and Comments
Total power loss minimization for IEEE-34 system (convergence curves)

## Slide 35
Results and Comments
Total power loss minimization for EDN system (case 1)
Items | Un-compensated (Case 0) | Compensated (Case 1) | 
Optimal locations and sizes of DGs (kW) | - | 21 | 1999.9
 |  | 25 | 2000
Total size | - | 3999.9 | 
Total losses (kW) | 805.73 | 542.459 | 
TVD | 0.0439 | 0.0225 | 
Minimum bus voltage(p.u.) | 0.9463 (#30) | 0.9669 (#23) | 
Maximum bus voltage(p.u.) | 0.9854 (#2) | 0.9874 (#2) | 
Overall power factor | 0.8457 | 0.7932 | 

## Slide 36
Results and Comments
Total power loss minimization for EDN system (case 2)
Items | Un-compensated (Case 0) | Compensated (Case 2) | 
Optimal locations and sizes of DGs (kW) | - | Locations | DG size (kW)
 |  | 25 | 2000
 |  | 21 | 2000
Total size | - | - | 4000
Total losses (kW) | 805.73 | 458.85 | 
TVD | 0.0439 | 0.0193 | 
Minimum bus voltage(p.u.) | 0.9463 (#30) | 0. 9699 (#23) | 
Maximum bus voltage(p.u.) | 0.9854 (#2) | 0.9879 (#2) | 
Overall power factor | 0.8457 | 0.8335 | 

## Slide 37
Results and Comments
Total power loss minimization for EDN system (case 1)

## Slide 38
Results and Comments
Total power loss minimization for EDN system (case 3)

## Slide 39
Results and Comments
Total power loss minimization for EDN system (case 1)

## Slide 40
Results and Comments
Total power loss minimization for EDN system (case 1)

## Slide 41
Results and Comments
Total power loss minimization for EDN system (case 1)

## Slide 42
CONCLUSIONS

## Slide 43
CONCLUSIONS
Efficient and accurate proposed procedure has been introduced to find the optimal placement of DGs and capacitors using proposed LSIs and BBA compared with other techniques.
Efficient proposed LSIs have been introduced to rank the load buses, based on two LSIs. However, the most sensitive buses are considered as the candidate buses for the installation of DGs and capacitors, while the most insensitive buses are not considered for the installation of DGs and capacitors.
The proposed LSIs have been characterized as; simple, efficient, accurate, non-iterative process, minimum time computation and suitable for large-scale power systems.
The optimal results using the proposed procedure have been compared with other methods, and have been proved that the capability of the proposed procedure to find the optimal solution of objective function with voltage profile and power factor improvement.
The BBA gives convergence curve with more accurate and efficient optimal placement of DGs and capacitors in distribution systems.

## Slide 44
The proposed BBA mathematical model is very simple since it has few parameters.
The BFS load flow algorithm has been used successfully for the load flow calculations.
The proposed procedure represents a potential tool to reduce the system losses and improve the voltage profile.
The proposed procedure has been tested on 34-bus radial distribution system. Moreover, a real distribution system of the East Delta Network (EDN) as a part of the UEN has been used to show the capability of proposed procedure.
Finally, enhancement the distribution system reliability has been used using DGs and/or capacitors. In addition, the importance of LSIs as proximity indicators for ordering the load buses to reduce the search space in the optimization procedure has been presented. Moreover, the proposed procedure represents a potential tool to improve the distribution system performance as well as help the system operators.

## Slide 45
APPENDIX - A
TEST SYSTEMS

## Slide 46
TEST SYSTEMS
34-Bus Distribution System

## Slide 47
Line No. | Sending bus | Receiving bus | R (Ω) | X (Ω)
1 | 1 | 2 | 0.1170 | 0.0480
2 | 2 | 3 | 0.1073 | 0.0440
3 | 3 | 4 | 0.1645 | 0.0457
4 | 4 | 5 | 0.1495 | 0.0415
5 | 5 | 6 | 0.1495 | 0.0415
6 | 6 | 7 | 0.3144 | 0.0540
7 | 7 | 8 | 0.2096 | 0.0360
8 | 8 | 9 | 0.3144 | 0.0540
9 | 9 | 10 | 0.2096 | 0.0360
10 | 10 | 11 | 0.1310 | 0.0225
11 | 11 | 12 | 0.1048 | 0.0180
12 | 3 | 13 | 0.1572 | 0.0270
13 | 13 | 14 | 0.2096 | 0.0360
14 | 14 | 15 | 0.1048 | 0.0180
15 | 15 | 16 | 0.0524 | 0.0090
16 | 6 | 17 | 0.1794 | 0.0498
17 | 17 | 18 | 0.1645 | 0.0457
18 | 18 | 19 | 0.2079 | 0.0473
19 | 19 | 20 | 0.1890 | 0.0430
20 | 20 | 21 | 0.1890 | 0.0430
21 | 21 | 22 | 0.2620 | 0.0450
22 | 22 | 23 | 0.2620 | 0.0450
23 | 23 | 24 | 0.3144 | 0.0540
24 | 24 | 25 | 0.2096 | 0.0360
25 | 25 | 26 | 0.1310 | 0.0225
26 | 26 | 27 | 0.1048 | 0.0180
27 | 7 | 28 | 0.1572 | 0.0270
28 | 28 | 29 | 0.1572 | 0.0270
29 | 29 | 30 | 0.1572 | 0.0270
30 | 10 | 31 | 0.1572 | 0.0270
31 | 31 | 32 | 0.2096 | 0.0360
32 | 32 | 33 | 0.1572 | 0.0270
33 | 33 | 34 | 0.1048 | 0.0180
Lines data for 34-bus distribution system

## Slide 48
Line No. | P (kW) | Q (kVAR)
1 | 0 | 0
2 | 230 | 142.5
3 | 0 | 0
4 | 230 | 142.5
5 | 230 | 142.5
6 | 0 | 0
7 | 0 | 0
8 | 230 | 142.5
9 | 230 | 142.5
10 | 0 | 0
11 | 230 | 142.5
12 | 137 | 84
13 | 72 | 45
14 | 72 | 45
15 | 72 | 45
16 | 13.5 | 7.5
17 | 230 | 142.5
18 | 230 | 142.5
19 | 230 | 142.5
20 | 230 | 142.5
21 | 230 | 142.5
22 | 230 | 142.5
23 | 230 | 142.5
24 | 230 | 142.5
25 | 230 | 142.5
26 | 230 | 142.5
27 | 137 | 85
28 | 75 | 48
29 | 75 | 48
30 | 75 | 48
31 | 57 | 34.5
32 | 57 | 34.5
33 | 57 | 34.5
34 | 57 | 34.5
Bus data for 34-bus distribution system

## Slide 49
East Delta Network (EDN) System
Single line diagram of the EDN distribution system

## Slide 50
Line No. | Sending bus | Receiving bus | R (Ω) | X (Ω) | Load at Receiving bus | 
 |  |  |  |  | P (kW) | Q (kVAR)
1 | 1 | 2 | 0.05630 | 0.031500 | 2875 | 1814
2 | 2 | 3 | 0.07155 | 0.025974 | 1100 | 695
3 | 3 | 4 | 0.01855 | 0.006734 | 1058 | 669
4 | 4 | 5 | 0.05565 | 0.020202 | 899 | 568
5 | 5 | 6 | 0.05300 | 0.019240 | 770 | 486
6 | 6 | 7 | 0.05300 | 0.019240 | 668 | 423
7 | 7 | 8 | 0.02120 | 0.007696 | 598 | 378
8 | 8 | 9 | 0.10070 | 0.036556 | 546 | 345
9 | 9 | 10 | 0.04505 | 0.016354 | 380 | 240
10 | 10 | 11 | 0.03975 | 0.014430 | 210 | 132
11 | 11 | 12 | 0.11130 | 0.040404 | 94.586 | 59.368
12 | 12 | 13 | 0.01325 | 0.004810 | 34.423 | 21.518
13 | 2 | 14 | 0.06360 | 0.023088 | 1772 | 1118
14 | 14 | 15 | 0.07155 | 0.025974 | 1640 | 1035
15 | 15 | 16 | 0.02650 | 0.009620 | 1452 | 915
16 | 16 | 17 | 0.01060 | 0.003848 | 1434 | 904
17 | 17 | 18 | 0.09275 | 0.033670 | 1212 | 765
18 | 18 | 19 | 0.01060 | 0.003848 | 1086 | 685
19 | 19 | 20 | 0.02650 | 0.009620 | 953 | 602
20 | 20 | 21 | 0.04505 | 0.016354 | 827 | 521
21 | 21 | 22 | 0.05300 | 0.019240 | 716 | 452
22 | 22 | 23 | 0.05300 | 0.019240 | 550 | 347
23 | 23 | 24 | 0.0663 | 0.0240 | 434 | 273
24 | 24 | 25 | 0.2253 | 0.0818 | 346 | 218
25 | 25 | 26 | 0.0265 | 0.0096 | 316 | 199
26 | 26 | 27 | 0.0265 | 0.0096 | 184 | 116
27 | 27 | 28 | 0.0133 | 0.0048 | 139 | 87.911
28 | 28 | 29 | 0.1723 | 0.0625 | 113 | 71.734
29 | 29 | 30 | 0.0080 | 0.0029 | 34.25 | 21.734
Buses and lines data for EDN distribution system

## Slide 51
APPENDIX - B
BACKWARD/FORWARD
SWEEP ALGORITHM

## Slide 52
The BFS algorithm involves mainly an iterative three basic steps
The three steps
the nodal current calculation,
the backward sweep
the forward sweep
The BFS algorithm
Step 1: Initialization
The distribution system line and load data.
The base power and base voltage.
Calculate the base impedance.
Calculate the per unit values of line and load data.
Take the voltage for all buses flat voltage (1 p.u.).
Set convergence tolerance Є=0.0001 and ΔVmax = 0.

## Slide 53
Step 2: Radial distribution system numbering scheme
Step 3: Nodal current calculation
Step 4: Backward sweep

## Slide 54
Step 5: Forward sweep
Step 6: Check the voltage mismatches
Step 7: Check stopping criterion
Step 8: Power loss calculation

## Slide 55
Flow chart of BFS algorithm

## Slide 56
Thank You